## Complete Building Method
2013 NACM | People | Occupancy Vent Factor | Sensible heat | Latent heat | Receptacle | Hot water | Lighting | Min. Vent per Area | Ventilation | Cooling UMLH Limit | Heating UMLH Limit | Gas Appl Load | Refrig Load | Schedule
| # per 1000 ft² |  | Btu/h per person | Btu/h per person | Load W/ft² | Gal/h per person | W/ft² | CFM/ft² | CFM/ft² | Hrs | Hrs | Btu/h-ft2 | W/ft2
Auditorium Building | 143 | 1 | 245 | 105 | 1 | 0.09 | 1.5 | 0.15 | 1.07 | 150 | 150 | 0 | 0 | Assembly
Classroom Building | 40 | 0.5 | 246 | 171 | 1 | 0.162 | 1.1 | 0.15 | 0.32 | 150 | 150 | 0 | 0 | School
Commercial and Industrial Storage Building | 5 | 0.5 | 268 | 403 | 0.43 | 0.162 | 0.6 | 0.15 | 0.15 | 150 | 150 | 0 | 0.28 | Warehouse
Convention Center Building | 136 | 0.5 | 245 | 112 | 0.96 | 0.086 | 1.2 | 0.15 | 1.02 | 150 | 150 | 0.04 | 0.03 | Assembly
Data Center Buildings (Note 9) | 5 | 0.5 | 268 | 403 | note 9 | 0.162 | 0.8 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | Data
Financial Institution Building | 10 | 0.5 | 250 | 250 | 1.5 | 0.18 | 1.1 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | Office
General Commercia' or Industrial Work Building | 7 | 0.5 | 375 | 625 | 1 | 0.18 | 1 | 0.15 | 0.15 | 150 | 150 | 0 | 0.28 | Manufacturing
Grocery Store Buildings | 29 | 0.5 | 252 | 225 | 0.91 | 0.17 | 1.5 | 0.15 | 0.22 | 150 | 150 | 0.03 | 0.14 | Retail
Library Building | 10 | 0.5 | 250 | 250 | 1.5 | 0.18 | 1.3 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | Office
Medical Building/Clinic Building | 10 | 0.5 | 250 | 213 | 1.18 | 0.165 | 1.1 | 0.15 | 0.15 | 150 | 150 | 0.33 | 1.12 | Health
Office Building | 10 | 0.5 | 250 | 206 | 1.34 | 0.159 | 0.8 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | Office
Parking Garage Building | 10 | 0.5 | 250 | 200 | 0 | 0 | 0.2 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | Parking
Religious Facility Building | 136 | 0.5 | 245 | 112 | 0.96 | 0.086 | 1.6 | 0.15 | 1.03 | 150 | 150 | 0.04 | 0 | Assembly
Restaurant Building | 45 | 0.5 | 274 | 334 | 0.79 | 0.549 | 1.2 | 0.15 | 0.38 | 150 | 150 | 5.14 | 0.06 | Restaurant
School Building | 40 | 0.5 | 246 | 171 | 1 | 0.162 | 1 | 0.15 | 0.32 | 150 | 150 | 0.04 | 0.03 | School
Theater Building | 130 | 1 | 268 | 403 | 0.54 | 0.09 | 1.3 | 0.15 | 0.98 | 150 | 150 | 0.04 | 0 | Assembly
All Other Buildings | 10 | 0.5 | 250 | 200 | 1 | 0.18 | 0.6 | 0.15 | 0.15 | 150 | 150 | 0.04 | 0.03 | Office
Note 9 - Receptacle Load shall be specified by the user.

## Area Category Method
2013 NACM Space Type | People | Occupancy Vent Factor | Sensible heat | Latent heat | Receptacle | Hot water | Lighting | Minimum Ventilation Per Area | Minimum Design Ventilation Per Area | Cooling UMLH Limit | Heating UMLH Limit | Gas Equipment Power | Refrig Load | Illuminance Setpoint for Daylighting |  | Primary Sidelit Daylighting Zone Setpoint Adjustment Factor | Secondary Sidelit Daylighting Zone Setpoint Adjustment Factor | Schedule | Space Function Index (BEM Enums index. Temporary, until new ruleset function 'SymbolValue' is online) | Notes | People (Pre-V3b) | Diff | Ventilation (Pre-V3b) | Diff
| # per 1000 ft² |  | per person | per person | Load W/ft² | Gal/h per person | W/ft² | CFM/ft² | CFM/ft² | Hrs | Hrs | Btu/h-ft2 | W/ft2 | Min (lux) | Max (lux) | [5 empty] | # per 1000 ft2
Auditorium Area | 142.8571 | 0.5 | 245 | 105 | 1 | 0.09 | 1.5 | 0.15 | 1.0714 | 150 | 150 | 0 | 0 | 50 | 1000 | 1.5 | 2 | Assembly | 101 |  | 143 | -0.14286 | 1.07 | 0.0014286
Auto Repair Area | 10 | 0.5 | 275 | 475 | 1 | 0.18 | 0.9 | 1.5 | 1.5 | 150 | 150 | 0.75064 | 0 | 200 | 1500 | 1.5 | 2 | Manufacturing | 102 |  | 10 | 0 | 1.5 | 0
Bar, Cocktail Lounge and Casino Areas | 66.6667 | 0.5 | 275 | 275 | 1 | 0.18 | 1.1 | 0.2 | 0.5 | 150 | 150 | 0 | 1.12 | 50 | 200 | 1.5 | 2 | Restaurant | 103 |  | 67 | -0.33333 | 0.2 | 0.3
Beauty Salon Area | 10 | 0.5 | 250 | 200 | 2 | 0.18 | 1.7 | 0.4 | 0.4 | 150 | 150 | 0 | 0 | 500 | 500 | 1.5 | 2 | Retail | 104 |  | 10 | 0 | 0.4 | 0
Classrooms, Lecture, Training, Vocational Areas | 50 | 0.5 | 245 | 155 | 1 | 0.18 | 1.2 | 0.15 | 0.375 | 150 | 150 | 0 | 0 | 50 | 500 | 1.5 | 2 | School | 105 |  | 50 | 0 | 0.38 | -0.005
Civic Meeting Place Area | 66.6667 | 0.5 | 250 | 200 | 1.5 | 0.18 | 1.3 | 0.15 | 0.5 | 150 | 150 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | 106 | DR 1/24/15 Revised occupancy from 25 to 67 per JA updates | 25 | 41.6667 | 0.19 | 0.31
Commercial and Industrial Storage Areas (conditioned or unconditioned) | 2 | 0.5 | 275 | 475 | 0.2 | 0.18 | 0.6 | 0.15 | 0.15 | 8760 | 8760 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | 107 | DR 2/18/15: Revised occupancy from 3 to 2 per CEC Review Instead of relaxed UMLH, use modified thermostat schedule? | 3 | -1 | 0.15 | 0
Commercial and Industrial Storage Areas (refrigerated) | 0 | 0.5 | 275 | 475 | 0.2 | 0.18 | 0.7 | 0.15 | 0.15 | 8760 | 8760 | 0 | 10 | 50 | 300 | 1.5 | 2 | Warehouse | 108 | Instead of relaxed UMLH, use modified thermostat schedule? | 0 | 0 | 0 | 0.15
Computer Room (Note 11) | 3 | 0.5 | 275 | 475 | 0 | 0.18 | 0.8 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 75 | 300 | 1 | 4 | Data | 109 | SpcFunc only valid if user-input receptacle load is >= 20W/ft2 | 3 | 0 | 0.15 | 0
Convention, Conference, Multipurpose and Meeting Center Areas (Note 10) | 66.6667 | 0.5 | 245 | 155 | 1 | 0.09 | 1.4 | 0.15 | 0.5 | 150 | 150 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | 110 |  | 67 | -0.33333 | 0.5 | 0
Corridors, Restrooms, Stairs, and Support Areas | 10 | 0.5 | 250 | 250 | 0.2 | 0 | 0.6 | 0.15 | 0.15 | 8760 | 8760 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | 111 | RLH: Hot water at zero on assumption that the occupancy in this space is double counting of people already counted in other spaces. Instead of relaxed UMLH, use modified thermostat schedule? | 10 | 0 | 0.15 | 0
Dining Area | 66.6667 | 0.5 | 275 | 275 | 0.5 | 0.578 | 1.1 | 0.15 | 0.5 | 150 | 150 | 0 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | 112 |  | 67 | -0.33333 | 0.5 | 0
Dry Cleaning (Coin Operated) | 10 | 0.5 | 250 | 250 | 3 | 0.18 | 0.9 | 0.3 | 0.3 | 150 | 150 | 0.75064 | 0 | 300 | 300 | 1.5 | 2 | Manufacturing | 113 |  | 10 | 0 | 0.3 | 0
Dry Cleaning (Full Service Commercial) | 10 | 0.5 | 250 | 250 | 3 | 0.18 | 0.9 | 0.45 | 0.45 | 150 | 150 | 0.75064 | 0 | 300 | 300 | 1.5 | 2 | Manufacturing | 114 |  | 10 | 0 | 0.45 | 0
Electrical, Mechanical, Telephone Rooms | 3 | 0.5 | 250 | 250 | 3 | 0.18 | 0.7 | 0.15 | 0.15 | 8760 | 8760 | 0 | 0 | 200 | 200 | 1 | 4 | Warehouse | 115 | Instead of relaxed UMLH, use modified thermostat schedule? | 3 | 0 | 0.15 | 0
Exercise Room | 20 | 0.5 | 255 | 875 | 0.5 | 0.18 | 1 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | 116 |  | 67 | -47 | 0.5 | -0.35
Exhibit, Museum Areas | 66.6667 | 0.5 | 250 | 250 | 1.5 | 0.09 | 2 | 0.15 | 0.5 | 150 | 150 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly | 117 |  | 67 | -0.33333 | 0.5 | 0
Financial Transaction Area | 10 | 0.5 | 250 | 250 | 1.5 | 0.18 | 1.2 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 100 | 300 | 1.5 | 2 | Office | 118 |  | 10 | 0 | 0.15 | 0
General Commercial and Industrial Work Areas, High Bay | 10 | 0.5 | 275 | 475 | 1 | 0.18 | 1 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | 119 |  | 10 | 0 | 0.15 | 0
General Commercial and Industrial Work Areas, Low Bay | 10 | 0.5 | 275 | 475 | 1 | 0.18 | 0.9 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | 120 |  | 10 | 0 | 0.15 | 0
General Commercial and Industrial Work Areas, Precision | 10 | 0.5 | 250 | 200 | 1 | 0.18 | 1.2 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 1000 | 3000 | 1.5 | 2 | Manufacturing | 121 |  | 10 | 0 | 0.15 | 0
Grocery Sales Areas | 33.3333 | 0.5 | 250 | 200 | 1 | 0.18 | 1.2 | 0.15 | 0.25 | 150 | 150 | 1.1942 | 2.6 | 500 | 500 | 1.5 | 2 | Retail | 122 |  | 33 | 0.33333 | 0.25 | 0
Gymnasium/Sports Arena | 66.6667 | 0.5 | 255 | 875 | 0.5 | 0.18 | 1 | 0.15 | 0.5 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | 201
High-Rise Residential Living Spaces (Note 9) | 5 | 0.5 | 245 | 155 | 0.5 | T24 RecircDHW | 0.5 | 0.06 | see NACM | 150 | 150 | 0.6824 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | 123 | DR 11/19/15: Revised VentPerArea to 0.06 per CEC | 5 | 0 | 0.15 | #VALUE!
Hotel Function Area | 142.8571 | 0.5 | 250 | 200 | 0.5 | 0.096 | 1.5 | 0.15 | 1.0714 | 150 | 150 | 0 | 0 | 50 | 300 | 1.5 | 2 | Assembly | 124 | DR 1/24/15 Revised occupancy from 67 to 143 per JA updates | 67 | 75.8571 | 0.5 | 0.57143
Hotel/Motel Guest Room (Note 9) | 5 | 0.5 | 245 | 155 | 0.5 | 4.48 | 0.5 | see NACM | see NACM | 150 | 150 | 0 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | 125 | DR 11/19/15: Revised VentPerArea to 0.06 per CEC | 5 | 0 | 0.15 | #VALUE!
Housing, Public and Common Areas: Multi-family, Dormitory | 20 | 0.5 | 250 | 250 | 0.5 | 0.192 | 1 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 200 | 500 | 1.5 | 2 | ResidentialCommon | 126 | DR 1/24/15 Revised occupancy from 10 to 20 per JA updates | 10 | 10 | 0.15 | 0
Housing, Public and Common Areas: Senior Housing | 10 | 0.5 | 250 | 250 | 0.5 | 0.192 | 1.5 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 400 | 1000 | 1.5 | 2 | ResidentialCommon | 127 |  | 10 | 0 | 0.15 | 0
Kitchen, Commercial Food Preparation | 5 | 0.5 | 275 | 475 | 1.5 | 0.578 | 1.6 | 0.15 | 0.15 | 150 | 150 | 17.5377 | 1.12 | 100 | 500 | 1.5 | 2 | Restaurant | 128 | GasEquipPwr only valid if hood length > 0. If there is an exhaust hood, set convective fraction to 0 | 5 | 0 | 0.15 | 0
Kitchenette or Residential Kitchen | 5 | 0.5 | 275 | 475 | 1 | 0.36 | 1.6 | 0.15 | 0.15 | 150 | 150 | 3 | 0.5 | 100 | 500 | 1.5 | 2 | Office | 129 |  | 5 | 0 | 0.15 | 0
Laboratory, Scientific | 10 | 0.5 | 250 | 200 | 2 | 0.18 | 1.4 | 0.15 | see NACM | 150 | 150 | 12.6926 | 0.28 | 500 | 1000 | 1.5 | 2 | Laboratory | 130 |  | 10 | 0
Laboratory, Equipment Room | 5 | 0.5 | 250 | 200 | 10 | 0.18 | 1.4 | 0.15 | see NACM | 150 | 150 | 12.6926 | 0 | 500 | 1000 | 1.5 | 2 | Laboratory | 131 |  | 5 | 0
Laundry | 10 | 0.5 | 250 | 250 | 3 | 0.578 | 0.9 | 0.15 | 0.15 | 8760 | 8760 | 0.75064 | 0 | 100 | 300 | 1.5 | 2 | Manufacturing | 132 |  | 10 | 0 | 0.15 | 0
Library, Reading Areas | 20 | 0.5 | 250 | 200 | 1.5 | 0.18 | 1.2 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 150 | 500 | 1.5 | 2 | Office | 133 |  | 20 | 0 | 0.15 | 0
Library, Stacks | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | 1.5 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 200 | 300 | 1 | 4 | Office | 134 |  | 10 | 0 | 0.15 | 0
Lobby, Hotel | 10 | 0.5 | 250 | 250 | 0.5 | 0.18 | 1.1 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | 135 | DR 2/18/15: Revised occupancy from 67 to 10 per CEC Review | 10 | 0 | 0.15 | 0
Lobby, Main Entry | 66.6667 | 0.5 | 250 | 250 | 0.5 | 0.09 | 1.5 | 0.15 | 0.5 | 150 | 150 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | 136 | DR 1/24/15 Revised occupancy from 10 to 67 per JA updates | 10 | 56.6667 | 0.15 | 0.35
Locker/Dressing Room | 20 | 0.5 | 255 | 475 | 0.5 | 0.578 | 0.8 | 0.15 | 0.15 | 8760 | 8760 | 0 | 0 | 20 | 200 | 1 | 4 | Assembly | 137 |  | 20 | 0 | 0.15 | 0
Lounge, Recreation | 66.6667 | 0.5 | 275 | 275 | 1 | 0.09 | 1.1 | 0.15 | 0.5 | 150 | 150 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly | 138 |  | 67 | -0.33333 | 0.5 | 0
Malls and Atria | 33.3333 | 0.5 | 250 | 250 | 0.5 | 0.18 | 1.2 | 0.15 | 0.25 | 150 | 150 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail | 139 | DR 1/24/15 Revised occupancy from 33.333 to 33 per JA updates | 33 | 0.33333 | 0.25 | 0
Medical and Clinical Care | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | 1.2 | 0.15 | 0.15 | 150 | 150 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | 140 |  | 10 | 0 | 0.15 | 0
Nurseries for Children - Day Care | 28.57 | 0.5 | 245 | 155 | 1 | 0.24 | 1.2 | 0.15 | 0.21428 | 150 | 150 | 0 | 0 | 50 | 500 | 1.5 | 2 | School | 202
Office (Greater than 250 square feet in floor area) | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | 0.75 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 75 | 500 | 1 | 4 | Office | 141 |  | 10 | 0 | 0.15 | 0
Office (250 square feet in floor area or less) | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | 1 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | Office | 142 |  | 10 | 0 | 0.15 | 0
Parking Garage Building, Parking Area | 5 | 0.5 | 250 | 200 | 0 | 0 | 0.14 | 0.75 | 0.75 | 8760 | 8760 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking | 143 | DR 2/18/15: Revised occupancy from 10 to 5 per CEC Review LF: 0.75 CFM/SF per 2010 CMC Table 4-4 Instead of relaxed UMLH, use modified thermostat schedule? | 10 | -5 | 0.75 | 0
Parking Garage Area Dedicated Ramps | 5 | 0.5 | 250 | 200 | 0 | 0 | 0.3 | 0.75 | 0.75 | 8760 | 8760 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking | 144 | DR 2/18/15: Revised occupancy from 10 to 5 per CEC Review LF: 0.75 CFM/SF per 2010 CMC Table 4-4 Instead of relaxed UMLH, use modified thermostat schedule? | 10 | -5 | 0.75 | 0
Parking Garage Area Daylight Adaptation Zones | 5 | 0.5 | 250 | 200 | 0 | 0 | 0.6 | 0.75 | 0.75 | 8760 | 8760 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking | 145 | DR 2/18/15: Revised occupancy from 10 to 5 per CEC Review LF: 0.75 CFM/SF per 2010 CMC Table 4-4 Instead of relaxed UMLH, use modified thermostat schedule? | 10 | -5 | 0.75 | 0
Police Station and Fire Station | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | 0.9 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 50 | 300 | 1.5 | 2 | ResidentialCommon | 146 |  | 10 | 0 | 0.15 | 0
Religious Worship Area | 142.8571 | 0.5 | 245 | 105 | 0.5 | 0.09 | 1.5 | 0.15 | 1.0714 | 150 | 150 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly | 147 |  | 143 | -0.14286 | 1.07 | 0.0014286
Retail Merchandise Sales, Wholesale Showroom | 33.3333 | 0.5 | 250 | 200 | 1 | 0.18 | 1.2 | 0.2 | 0.25 | 150 | 150 | 0 | 0 | 100 | 1000 | 1.5 | 2 | Retail | 148 |  | 33 | 0.33333 | 0.2 | 0.05
Theater, Motion Picture | 142.8571 | 0.5 | 245 | 105 | 0.5 | 0.09 | 0.9 | 0.15 | 1.0714 | 150 | 150 | 0 | 0 | 2 | 50 | 1.5 | 2 | Assembly | 150 |  | 143 | -0.14286 | 1.07 | 0.0014286
Theater, Performance | 142.8571 | 0.5 | 245 | 105 | 0.5 | 0.09 | 1.4 | 0.15 | 1.0714 | 150 | 150 | 0 | 0 | 2 | 200 | 1.5 | 2 | Assembly | 151 |  | 143 | -0.14286 | 1.07 | 0.0014286
Transportation Function | 33.3333 | 0.5 | 250 | 250 | 0.5 | 0.18 | 1.2 | 0.15 | 0.25 | 150 | 150 | 0 | 0 | 50 | 500 | 1.5 | 2 | Assembly | 152 |  | 33 | 0.33333 | 0.25 | 0
Unleased Tenant Area | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | 0.6 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 75 | 500 | 1 | 4 | Office | 203
Unoccupied-Exclude from Gross Floor Area | 0 | 0.5 | 250 | 250 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | 99 | Instead of relaxed UMLH, use modified thermostat schedule? | 0 | 0 | 0 | 0
Unoccupied-Include in Gross Floor Area | 0 | 0.5 | 250 | 250 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | 98 | Instead of relaxed UMLH, use modified thermostat schedule? | 0 | 0 | 0 | 0
Videoconferencing Studio (Note S1) | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | 1.2 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office | 153 |  | 10 | 0 | 0.15 | 0
Waiting Area | 66.6667 | 0.5 | 250 | 250 | 0.5 | 0.18 | 1.1 | 0.15 | 0.5 | 150 | 150 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office | 154 | DR 2/18/15 Revised occupancy from 10 to 67 per CEC review | 10 | 56.6667 | 0.15 | 0.35
All Others (including unleased tenant space in multi-tenant facilities) | 10 | 0.5 | 250 | 200 | 1 | 0.18 | 0.6 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 100 | 300 | 1.5 | 2 | Office | 157 |  | 10 | 0 | 0.15 | 0
| Note 7: |  | Refer to the Residential ACM, Appendix E for determining residential hot water load
| Note 11. |  | For data centers the process load from the servers and UPS shall be as designed, with the baseline same as proposed.
| Note S1: |  | Videoconferencing studios may install up to an additional 1.5 W/ft2 for videoconferencing rooms that meet all requirements in section 140.6(c)2Gvii.

## For CSV Generation
// This table pasted into App5-4A_SpaceBySpace.csv
TABLE SpaceFunctionData
| FuncType | OccDens | OccVentFrac | OccSensHtRt | OccLatHtRt | RecptPwrDens | HotWtrHtgRt | IntLPDReg | CodeVentPerArea | CodeTotalVentPerArea | ClgUMLHLimit | HtgUMLHLimit | GasEqpPwrDens | CommRfrgEPD | IllumSetptMin | IllumSetptMax | IllumSetptAdjFacPri | IllumSetptAdjFacSec | FuncSchGrp | OccSchRef | RecptSchRef | HotWtrHtgSchRef | IntLtgRegSchRef | GasEqpSchRef | CommRfrgEqpSchRef | InfSchRef | AvailSchRef | HtgTstatSchRef | ClgTstatSchRef | ElevSchRef | EscalSchRef | WtrHtrTempSetptSchRef | SpcFuncIdx | ;
| //SpaceBySpace | # per 1000 ft² |  | Btu / occupant | Btu / occupant | Load W/ft² | Gal/h per person | W/ft² | CFM/ft² | CFM/ft² | Hrs | Hrs | Btu/h-ft2 | W/ft2 | lux | lux |  |  |  | Occupancy Schedule | Receptacle Schedule | Hot Water Schedule | Regulated Lighting Schedule | Gas Equipment Schedule | Refrigeration Schedule | Infiltration Schedule | Availability Sched | Heating Setpoint Schedule (F) | Cooling Setpoint Schedule (F) | Elevator Schedule | Escalator Schedule | Water Heater Temperature Setpoint Schedule |  | ;
| Auditorium Area | 142.86 | 0.5 | 245 | 105 | 1 | 0.09 | 1.5 | 0.15 | 1.0714 | 150 | 150 | 0 | 0 | 50 | 1000 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 101 | ;
| Auto Repair Area | 10 | 0.5 | 275 | 475 | 1 | 0.18 | 0.9 | 1.5 | 1.5 | 150 | 150 | 0.75064 | 0 | 200 | 1500 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | 102 | ;
| Bar, Cocktail Lounge and Casino Areas | 66.67 | 0.5 | 275 | 275 | 1 | 0.18 | 1.1 | 0.2 | 0.5 | 150 | 150 | 0 | 1.12 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | 103 | ;
| Beauty Salon Area | 10 | 0.5 | 250 | 200 | 2 | 0.18 | 1.7 | 0.4 | 0.4 | 150 | 150 | 0 | 0 | 500 | 500 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | 104 | ;
| Classrooms, Lecture, Training, Vocational Areas | 50 | 0.5 | 245 | 155 | 1 | 0.18 | 1.2 | 0.15 | 0.375 | 150 | 150 | 0 | 0 | 50 | 500 | 1.5 | 2 | School | SchoolOccupancy | SchoolReceptacle | SchoolServiceHotWater | SchoolLights | SchoolGasEquip | SchoolRefrigeration | SchoolInfiltration | SchoolHVACAvail | SchoolHtgSetpt | SchoolClgSetpt | SchoolElevator | SchoolEscalator | SchoolWtrHtrSetpt | 105 | ;
| Civic Meeting Place Area | 66.67 | 0.5 | 250 | 200 | 1.5 | 0.18 | 1.3 | 0.15 | 0.5 | 150 | 150 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 106 | ;
| Commercial and Industrial Storage Areas (conditioned or unconditioned) | 2 | 0.5 | 275 | 475 | 0.2 | 0.18 | 0.6 | 0.15 | 0.15 | 8760 | 8760 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | 107 | ;
| Commercial and Industrial Storage Areas (refrigerated) | 0 | 0.5 | 275 | 475 | 0.2 | 0.18 | 0.7 | 0.15 | 0.15 | 8760 | 8760 | 0 | 10 | 50 | 300 | 1.5 | 2 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | 108 | ;
| Computer Room | 3 | 0.5 | 275 | 475 | 20 | 0.18 | 0.8 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 75 | 300 | 1 | 4 | Data | DataOccupancy | DataReceptacle | DataServiceHotWater | DataLights | DataGasEquip | DataRefrigeration | DataInfiltration | DataHVACAvail | DataHtgSetpt | DataClgSetpt | DataElevator | DataEscalator | DataWtrHtrSetpt | 109 | ;
| Convention, Conference, Multipurpose and Meeting Center Areas | 66.67 | 0.5 | 245 | 155 | 1 | 0.09 | 1.4 | 0.15 | 0.5 | 150 | 150 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 110 | ;
| Corridors, Restrooms, Stairs, and Support Areas | 10 | 0.5 | 250 | 250 | 0.2 | 0 | 0.6 | 0.15 | 0.15 | 8760 | 8760 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 111 | ;
| Dining Area | 66.67 | 0.5 | 275 | 275 | 0.5 | 0.578 | 1.1 | 0.15 | 0.5 | 150 | 150 | 0 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | 112 | ;
| Dry Cleaning (Coin Operated) | 10 | 0.5 | 250 | 250 | 3 | 0.18 | 0.9 | 0.3 | 0.3 | 150 | 150 | 0.75064 | 0 | 300 | 300 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | 113 | ;
| Dry Cleaning (Full Service Commercial) | 10 | 0.5 | 250 | 250 | 3 | 0.18 | 0.9 | 0.45 | 0.45 | 150 | 150 | 0.75064 | 0 | 300 | 300 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | 114 | ;
| Electrical, Mechanical, Telephone Rooms | 3 | 0.5 | 250 | 250 | 3 | 0.18 | 0.7 | 0.15 | 0.15 | 8760 | 8760 | 0 | 0 | 200 | 200 | 1 | 4 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | 115 | ;
| Exercise Room | 20 | 0.5 | 255 | 875 | 0.5 | 0.18 | 1 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | 116 | ;
| Exhibit, Museum Areas | 66.67 | 0.5 | 250 | 250 | 1.5 | 0.09 | 2 | 0.15 | 0.5 | 150 | 150 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 117 | ;
| Financial Transaction Area | 10 | 0.5 | 250 | 250 | 1.5 | 0.18 | 1.2 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 100 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 118 | ;
| General Commercial and Industrial Work Areas, High Bay | 10 | 0.5 | 275 | 475 | 1 | 0.18 | 1 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | 119 | ;
| General Commercial and Industrial Work Areas, Low Bay | 10 | 0.5 | 275 | 475 | 1 | 0.18 | 0.9 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | 120 | ;
| General Commercial and Industrial Work Areas, Precision | 10 | 0.5 | 250 | 200 | 1 | 0.18 | 1.2 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 1000 | 3000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | 121 | ;
| Grocery Sales Areas | 33.33 | 0.5 | 250 | 200 | 1 | 0.18 | 1.2 | 0.15 | 0.25 | 150 | 150 | 1.1942 | 2.6 | 500 | 500 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | 122 | ;
| Gymnasium/Sports Arena | 66.67 | 0.5 | 255 | 875 | 0.5 | 0.18 | 1 | 0.15 | 0.5 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | 201 | ;
| High-Rise Residential Living Spaces | 5 | 0.5 | 245 | 155 | 0.5 | 0 | 0.5 | 0.06 | 0 | 150 | 150 | 0.6824 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | ResidentialLivingOccupancy | ResidentialLivingReceptacle | ResidentialLivingServiceHotWater | ResidentialLivingLights | ResidentialLivingGasEquip | ResidentialLivingRefrigeration | ResidentialLivingInfiltration | ResidentialLivingHVACAvail | ResidentialLivingHtgSetpt | ResidentialLivingClgSetpt | ResidentialLivingElevator | ResidentialLivingEscalator | ResidentialLivingWtrHtrSetpt | 123 | ;
| Hotel Function Area | 142.86 | 0.5 | 250 | 200 | 0.5 | 0.096 | 1.5 | 0.15 | 1.0714 | 150 | 150 | 0 | 0 | 50 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 124 | ;
| Hotel/Motel Guest Room | 5 | 0.5 | 245 | 155 | 0.5 | 4.48 | 0.5 | 0.06 | 0 | 150 | 150 | 0 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | ResidentialLivingOccupancy | ResidentialLivingReceptacle | ResidentialLivingServiceHotWater | ResidentialLivingLights | ResidentialLivingGasEquip | ResidentialLivingRefrigeration | ResidentialLivingInfiltration | ResidentialLivingHVACAvail | ResidentialLivingHtgSetpt | ResidentialLivingClgSetpt | ResidentialLivingElevator | ResidentialLivingEscalator | ResidentialLivingWtrHtrSetpt | 125 | ;
| Housing, Public and Common Areas: Multi-family, Dormitory | 20 | 0.5 | 250 | 250 | 0.5 | 0.192 | 1 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 200 | 500 | 1.5 | 2 | ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt | 126 | ;
| Housing, Public and Common Areas: Senior Housing | 10 | 0.5 | 250 | 250 | 0.5 | 0.192 | 1.5 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 400 | 1000 | 1.5 | 2 | ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt | 127 | ;
| Kitchen, Commercial Food Preparation | 5 | 0.5 | 275 | 475 | 1.5 | 0.578 | 1.6 | 0.15 | 0.15 | 150 | 150 | 17.5377 | 1.12 | 100 | 500 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | 128 | ;
| Kitchenette or Residential Kitchen | 5 | 0.5 | 275 | 475 | 1 | 0.36 | 1.6 | 0.15 | 0.15 | 150 | 150 | 3 | 0.5 | 100 | 500 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 129 | ;
| Laboratory, Scientific | 10 | 0.5 | 250 | 200 | 2 | 0.18 | 1.4 | 0.15 | 0 | 150 | 150 | 12.6926 | 0.28 | 500 | 1000 | 1.5 | 2 | Laboratory | LabOccupancy | LabReceptacle | LabServiceHotWater | LabLights | LabGasEquip | LabRefrigeration | LabInfiltration | LabHVACAvail | LabHtgSetpt | LabClgSetpt | LabElevator | LabEscalator | LabWtrHtrSetpt | 130 | ;
| Laboratory, Equipment Room | 5 | 0.5 | 250 | 200 | 10 | 0.18 | 1.4 | 0.15 | 0 | 150 | 150 | 12.6926 | 0 | 500 | 1000 | 1.5 | 2 | Laboratory | LabOccupancy | LabReceptacle | LabServiceHotWater | LabLights | LabGasEquip | LabRefrigeration | LabInfiltration | LabHVACAvail | LabHtgSetpt | LabClgSetpt | LabElevator | LabEscalator | LabWtrHtrSetpt | 131 | ;
| Laundry | 10 | 0.5 | 250 | 250 | 3 | 0.578 | 0.9 | 0.15 | 0.15 | 8760 | 8760 | 0.75064 | 0 | 100 | 300 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | 132 | ;
| Library, Reading Areas | 20 | 0.5 | 250 | 200 | 1.5 | 0.18 | 1.2 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 150 | 500 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 133 | ;
| Library, Stacks | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | 1.5 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 200 | 300 | 1 | 4 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 134 | ;
| Lobby, Hotel | 10 | 0.5 | 250 | 250 | 0.5 | 0.18 | 1.1 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 135 | ;
| Lobby, Main Entry | 66.67 | 0.5 | 250 | 250 | 0.5 | 0.09 | 1.5 | 0.15 | 0.5 | 150 | 150 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 136 | ;
| Locker/Dressing Room | 20 | 0.5 | 255 | 475 | 0.5 | 0.578 | 0.8 | 0.15 | 0.15 | 8760 | 8760 | 0 | 0 | 20 | 200 | 1 | 4 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 137 | ;
| Lounge, Recreation | 66.67 | 0.5 | 275 | 275 | 1 | 0.09 | 1.1 | 0.15 | 0.5 | 150 | 150 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 138 | ;
| Malls and Atria | 33.33 | 0.5 | 250 | 250 | 0.5 | 0.18 | 1.2 | 0.15 | 0.25 | 150 | 150 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | 139 | ;
| Medical and Clinical Care | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | 1.2 | 0.15 | 0.15 | 150 | 150 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | 140 | ;
| Nurseries for Children - Day Care | 28.57 | 0.5 | 245 | 155 | 1 | 0.24 | 1.2 | 0.15 | 0.21428 | 150 | 150 | 0 | 0 | 50 | 500 | 1.5 | 2 | School | SchoolOccupancy | SchoolReceptacle | SchoolServiceHotWater | SchoolLights | SchoolGasEquip | SchoolRefrigeration | SchoolInfiltration | SchoolHVACAvail | SchoolHtgSetpt | SchoolClgSetpt | SchoolElevator | SchoolEscalator | SchoolWtrHtrSetpt | 202 | ;
| Office (Greater than 250 square feet in floor area) | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | 0.75 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 75 | 500 | 1 | 4 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 141 | ;
| Office (250 square feet in floor area or less) | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | 1 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 142 | ;
| Parking Garage Building, Parking Area | 5 | 0.5 | 250 | 200 | 0 | 0 | 0.14 | 0.75 | 0.75 | 8760 | 8760 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking | ParkingOccupancy | ParkingReceptacle | ParkingServiceHotWater | ParkingLights | ParkingGasEquip | ParkingRefrigeration | ParkingInfiltration | ParkingHVACAvail | ParkingHtgSetpt | ParkingClgSetpt | ParkingElevator | ParkingEscalator | ParkingWtrHtrSetpt | 143 | ;
| Parking Garage Area Dedicated Ramps | 5 | 0.5 | 250 | 200 | 0 | 0 | 0.3 | 0.75 | 0.75 | 8760 | 8760 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking | ParkingOccupancy | ParkingReceptacle | ParkingServiceHotWater | ParkingLights | ParkingGasEquip | ParkingRefrigeration | ParkingInfiltration | ParkingHVACAvail | ParkingHtgSetpt | ParkingClgSetpt | ParkingElevator | ParkingEscalator | ParkingWtrHtrSetpt | 144 | ;
| Parking Garage Area Daylight Adaptation Zones | 5 | 0.5 | 250 | 200 | 0 | 0 | 0.6 | 0.75 | 0.75 | 8760 | 8760 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking | ParkingOccupancy | ParkingReceptacle | ParkingServiceHotWater | ParkingLights | ParkingGasEquip | ParkingRefrigeration | ParkingInfiltration | ParkingHVACAvail | ParkingHtgSetpt | ParkingClgSetpt | ParkingElevator | ParkingEscalator | ParkingWtrHtrSetpt | 145 | ;
| Police Station and Fire Station | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | 0.9 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 50 | 300 | 1.5 | 2 | ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt | 146 | ;
| Religious Worship Area | 142.86 | 0.5 | 245 | 105 | 0.5 | 0.09 | 1.5 | 0.15 | 1.0714 | 150 | 150 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 147 | ;
| Retail Merchandise Sales, Wholesale Showroom | 33.33 | 0.5 | 250 | 200 | 1 | 0.18 | 1.2 | 0.2 | 0.25 | 150 | 150 | 0 | 0 | 100 | 1000 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | 148 | ;
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | ;
| Theater, Motion Picture | 142.86 | 0.5 | 245 | 105 | 0.5 | 0.09 | 0.9 | 0.15 | 1.0714 | 150 | 150 | 0 | 0 | 2 | 50 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 150 | ;
| Theater, Performance | 142.86 | 0.5 | 245 | 105 | 0.5 | 0.09 | 1.4 | 0.15 | 1.0714 | 150 | 150 | 0 | 0 | 2 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 151 | ;
| Transportation Function | 33.33 | 0.5 | 250 | 250 | 0.5 | 0.18 | 1.2 | 0.15 | 0.25 | 150 | 150 | 0 | 0 | 50 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 152 | ;
| Unleased Tenant Area | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | 0.6 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 75 | 500 | 1 | 4 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 203 | ;
| Unoccupied-Exclude from Gross Floor Area | 0 | 0.5 | 250 | 250 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | UnoccupiedOccupancy | UnoccupiedReceptacle | UnoccupiedServiceHotWater | UnoccupiedLights | UnoccupiedGasEquip | UnoccupiedRefrigeration | UnoccupiedInfiltration | UnoccupiedHVACAvail | UnoccupiedHtgSetpt | UnoccupiedClgSetpt | UnoccupiedElevator | UnoccupiedEscalator | UnoccupiedWtrHtrSetpt | 99 | ;
| Unoccupied-Include in Gross Floor Area | 0 | 0.5 | 250 | 250 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | UnoccupiedOccupancy | UnoccupiedReceptacle | UnoccupiedServiceHotWater | UnoccupiedLights | UnoccupiedGasEquip | UnoccupiedRefrigeration | UnoccupiedInfiltration | UnoccupiedHVACAvail | UnoccupiedHtgSetpt | UnoccupiedClgSetpt | UnoccupiedElevator | UnoccupiedEscalator | UnoccupiedWtrHtrSetpt | 98 | ;
| Videoconferencing Studio | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | 1.2 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 153 | ;
| Waiting Area | 66.67 | 0.5 | 250 | 250 | 0.5 | 0.18 | 1.1 | 0.15 | 0.5 | 150 | 150 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 154 | ;
| All Others (including unleased tenant space in multi-tenant facilities) | 10 | 0.5 | 250 | 200 | 1 | 0.18 | 0.6 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | 100 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 157 | ;
ENDTABLE
//
// This table pasted into App5-4A_CompleteBuilding.csv
TABLE BldgUseData
| BldgType | OccDens | OccVentFrac | OccSensHtRt | OccLatHtRt | RecptPwrDens | HotWtrHtgRt | IntLPDReg | CodeVentPerArea | CodeTotalVentPerArea | ClgUMLHLimit | HtgUMLHLimit | GasEqpPwrDens | CommRfrgEPD | IllumSetptMin | IllumSetptMax | IllumSetptAdjFacPri | IllumSetptAdjFacSec | FuncSchGrp | OccSchRef | RecptSchRef | HotWtrHtgSchRef | IntLtgRegSchRef | GasEqpSchRef | CommRfrgEqpSchRef | InfSchRef | AvailSchRef | HtgTstatSchRef | ClgTstatSchRef | ElevSchRef | EscalSchRef | WtrHtrTempSetptSchRef
| //Complete Building | # per 1000 ft² |  | Btu / occupant | Btu / occupant | Load W/ft² | Gal/h per person | W/ft² | CFM/ft² | CFM/ft² | Hrs | Hrs | Btu/h-ft2 | W/ft2 | lux | lux |  |  | 0 | Occupancy Schedule | Receptacle Schedule | Hot Water Schedule | Regulated Lighting Schedule | Gas Equipment Schedule | Refrigeration Schedule | Infiltration Schedule | Availability Sched | Heating Setpoint Schedule (F) | Cooling Setpoint Schedule (F) | Elevator Schedule | Escalator Schedule | Water Heater Temperature Setpoint Schedule
| Auditorium Building | 143 | 1 | 245 | 105 | 1 | 0.09 | 1.5 | 0.15 | 1.07 | 150 | 150 | 0 | 0 | NA | NA | NA | NA | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt
| Classroom Building | 40 | 0.5 | 246 | 171 | 1 | 0.162 | 1.1 | 0.15 | 0.32 | 150 | 150 | 0 | 0 | NA | NA | NA | NA | School | SchoolOccupancy | SchoolReceptacle | SchoolServiceHotWater | SchoolLights | SchoolGasEquip | SchoolRefrigeration | SchoolInfiltration | SchoolHVACAvail | SchoolHtgSetpt | SchoolClgSetpt | SchoolElevator | SchoolEscalator | SchoolWtrHtrSetpt
| Commercial and Industrial Storage Building | 5 | 0.5 | 268 | 403 | 0.43 | 0.162 | 0.6 | 0.15 | 0.15 | 150 | 150 | 0 | 0.28 | NA | NA | NA | NA | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt
| Convention Center Building | 136 | 0.5 | 245 | 112 | 0.96 | 0.086 | 1.2 | 0.15 | 1.02 | 150 | 150 | 0.04 | 0.03 | NA | NA | NA | NA | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt
| Data Center Buildings | 5 | 0.5 | 268 | 403 | 20 | 0.162 | 0.8 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | NA | NA | NA | NA | Data | DataOccupancy | DataReceptacle | DataServiceHotWater | DataLights | DataGasEquip | DataRefrigeration | DataInfiltration | DataHVACAvail | DataHtgSetpt | DataClgSetpt | DataElevator | DataEscalator | DataWtrHtrSetpt
| Financial Institution Building | 10 | 0.5 | 250 | 250 | 1.5 | 0.18 | 1.1 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | NA | NA | NA | NA | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt
| General Commercia' or Industrial Work Building | 7 | 0.5 | 375 | 625 | 1 | 0.18 | 1 | 0.15 | 0.15 | 150 | 150 | 0 | 0.28 | NA | NA | NA | NA | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt
| Grocery Store Buildings | 29 | 0.5 | 252 | 225 | 0.91 | 0.17 | 1.5 | 0.15 | 0.22 | 150 | 150 | 0.03 | 1.8 | NA | NA | NA | NA | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt
| Library Building | 10 | 0.5 | 250 | 250 | 1.5 | 0.18 | 1.3 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | NA | NA | NA | NA | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt
| Medical Building/Clinic Building | 10 | 0.5 | 250 | 213 | 1.18 | 0.165 | 1.1 | 0.15 | 0.15 | 150 | 150 | 0.33 | 1.12 | NA | NA | NA | NA | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt
| Office Building | 10 | 0.5 | 250 | 206 | 1.34 | 0.159 | 0.8 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | NA | NA | NA | NA | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt
| Parking Garage Building | 10 | 0.5 | 250 | 200 | 0 | 0 | 0.2 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | NA | NA | NA | NA | Parking | ParkingOccupancy | ParkingReceptacle | ParkingServiceHotWater | ParkingLights | ParkingGasEquip | ParkingRefrigeration | ParkingInfiltration | ParkingHVACAvail | ParkingHtgSetpt | ParkingClgSetpt | ParkingElevator | ParkingEscalator | ParkingWtrHtrSetpt
| Religious Facility Building | 136 | 0.5 | 245 | 112 | 0.96 | 0.086 | 1.6 | 0.15 | 1.03 | 150 | 150 | 0.04 | 0 | NA | NA | NA | NA | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt
| Restaurant Building | 45 | 0.5 | 274 | 334 | 0.79 | 0.549 | 1.2 | 0.15 | 0.38 | 150 | 150 | 5.14 | 0.06 | NA | NA | NA | NA | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt
| School Building | 40 | 0.5 | 246 | 171 | 1 | 0.162 | 1 | 0.15 | 0.32 | 150 | 150 | 0.04 | 0.03 | NA | NA | NA | NA | School | SchoolOccupancy | SchoolReceptacle | SchoolServiceHotWater | SchoolLights | SchoolGasEquip | SchoolRefrigeration | SchoolInfiltration | SchoolHVACAvail | SchoolHtgSetpt | SchoolClgSetpt | SchoolElevator | SchoolEscalator | SchoolWtrHtrSetpt
| Theater Building | 130 | 1 | 268 | 403 | 0.54 | 0.09 | 1.3 | 0.15 | 0.98 | 150 | 150 | 0.04 | 0 | NA | NA | NA | NA | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt
| All Other Buildings | 10 | 0.5 | 250 | 200 | 1 | 0.18 | 0.6 | 0.15 | 0.15 | 150 | 150 | 0.04 | 0.03 | NA | NA | NA | NA | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt
ENDTABLE
// | [19 empty] | Occupancy | Receptacle | ServiceHotWater | Lights | GasEquip | Refrigeration | Infiltration | HVACAvail | HtgSetpt | ClgSetpt | Elevator | Escalator | WtrHtrSetpt

## FuncSchGrp Table
// Schedule names by Space:FunctionScheduleGroup
TABLE SpaceFunctionGroups
| FuncGroup | OccSchRef | RecptSchRef | HotWtrHtgSchRef | IntLtgRegSchRef | ProcGasSchRef | CommRfrgEqpSchRef | InfSchRef | AvailSchRef | HtgTstatSchRef | ClgTstatSchRef | ElevSchRef | EscalSchRef | WtrHtrTempSetptSchRef
// | Function Group Name | Occupancy Schedule | Receptacle Schedule | Hot Water Schedule | Regulated Lighting Schedule | Process Gas Schedule | Refrigeration Schedule | Infiltration Schedule | Availability Sched | Heating Setpoint Schedule (F) | Cooling Setpoint Schedule (F) | Elevator Schedule | Escalator Schedule | Water Heater Temperature Setpoint Schedule
| Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt
| Data | DataOccupancy | DataReceptacle | DataServiceHotWater | DataLights | DataGasEquip | DataRefrigeration | DataInfiltration | DataHVACAvail | DataHtgSetpt | DataClgSetpt | DataElevator | DataEscalator | DataWtrHtrSetpt
| Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt
| Laboratory | LabOccupancy | LabReceptacle | LabServiceHotWater | LabLights | LabGasEquip | LabRefrigeration | LabInfiltration | LabHVACAvail | LabHtgSetpt | LabClgSetpt | LabElevator | LabEscalator | LabWtrHtrSetpt
| Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt
| Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt
| Parking | ParkingOccupancy | ParkingReceptacle | ParkingServiceHotWater | ParkingLights | ParkingGasEquip | ParkingRefrigeration | ParkingInfiltration | ParkingHVACAvail | ParkingHtgSetpt | ParkingClgSetpt | ParkingElevator | ParkingEscalator | ParkingWtrHtrSetpt
| ResidentialLiving | ResidentialLivingOccupancy | ResidentialLivingReceptacle | ResidentialLivingServiceHotWater | ResidentialLivingLights | ResidentialLivingGasEquip | ResidentialLivingRefrigeration | ResidentialLivingInfiltration | ResidentialLivingHVACAvail | ResidentialLivingHtgSetpt | ResidentialLivingClgSetpt | ResidentialLivingElevator | ResidentialLivingEscalator | ResidentialLivingWtrHtrSetpt
| ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt
| Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt
| Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt
| School | SchoolOccupancy | SchoolReceptacle | SchoolServiceHotWater | SchoolLights | SchoolGasEquip | SchoolRefrigeration | SchoolInfiltration | SchoolHVACAvail | SchoolHtgSetpt | SchoolClgSetpt | SchoolElevator | SchoolEscalator | SchoolWtrHtrSetpt
| Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt
ENDTABLE

## CBC Table (hidden)
| Occupancy |  | Use | CBC Occupancy Load (ft²/occ) |  | CBC Occupancy Load | CBC Based Ventilation (cfm/ft²)7 | Ventilation from Table 121-A (cfm/ft²)
[6 empty] | (occ/1000 ft²)6 |  |  | Code: Standards 120.1(b)
1) | Aircraft Hangars |  |  | 500 |  | 2 | 0.015 | 0.15
2) | Auction Rooms |  |  | See Section 1004.7 |  |  |  | 0.15 | 2. Mechanical ventilation. Each space that is not naturally ventilated under Item 1 above shall be ventilated
3) | Assembly Areas (Concentrated Use) | [7 empty] | with a mechanical system capable of providing an outdoor air rate no less than the larger of:
|  | Auditoriums |  | See Section 1004.7 |  |  |  | 0.15 | A. The conditioned floor area of the space times the applicable ventilation rate from TABLE 120.1-A; or
|  | Bowling Alleys |  | 5 persons per lane |  |  |  | 0.15 | B. 15 cfm per person times the expected number of occupants.
|  | Churches & Chapels (Religious Worship) |  | 7 |  | 142.8571 | 1.0714 | 0.15 | For meeting the requirement in Section 120.1(b)2B for spaces without fixed seating, the expected
|  | Dance Floors |  | 5 |  | 200 | 1.5 | 1.15 | number of occupants shall be either the expected number specified by the building designer or one half
|  | Lobbies |  | 15 |  | 66.6667 | 0.5 | 2.15 | of the maximum occupant load assumed for egress purposes in the CBC, whichever is greater. For
|  | Lodge Rooms |  | 7 |  | 142.8571 | 1.0714 | 3.15 | spaces with fixed seating, the expected number of occupants shall be determined in accordance with the
|  | Reviewing Stands |  | 15 |  | 66.6667 | 0.5 | 4.15 | CBC.
|  | Stadiums |  | See Section 1004.7 |  |  |  | 0.15
|  | Theaters - All |  | See Section 1004.7 |  |  |  | 0.15
|  | Waiting Areas |  | 15 |  | 66.6667 | 0.5 | 4.15
4) | Assembly Areas (Nonconcentrated Use) |  |  | 15 |  | 66.6667 | 0.5 | 4.15
|  | Conference & Meeting Rooms 1 |  | 15 |  | 66.6667 | 0.5 | 4.15
|  | Dining Rooms/Areas |  | 15 |  | 66.6667 | 0.5 | 4.15
|  | Drinking Establishments 2 |  | 15 |  | 66.6667 | 0.5 | 4.15
|  | Exhibit/Display Areas |  | 15 |  | 66.6667 | 0.5 | 4.15
|  | Gymnasiums/Sports Arenas |  | 15 |  | 66.6667 | 0.5 | 4.15
|  | Lounges |  | 15 |  | 66.6667 | 0.5 | 4.15
|  | Stages |  | 15 |  | 66.6667 | 0.5 | 4.15
|  | Gaming, Keno, Slot Machine and Live Games Areas |  | 11 |  | 90.9091 | 0.68182 | 4.15
5) | Auto Repair Workshops |  |  | 100 |  | 10 | 0.075 | 4.15
6) | Barber & Beauty Shops |  |  | 100 |  | 10 | 0.075 | 4.15
7) | Children's Homes & Homes for Aged |  |  | 120 |  | 8.3333 | 0.0625 | 4.15
8) | Classrooms |  |  | 20 |  | 50 | 0.375 | 4.15
9) | Courtrooms |  |  | 40 |  | 25 | 0.1875 | 4.15
10) | Dormitories |  |  | 50 |  | 20 | 0.15 | 4.15
11) | Dry Cleaning (Coin-Operated) |  |  | 100 |  | 10 | 0.075 | 4.15
12) | Dry Cleaning (Commercial) |  |  | 100 |  | 10 | 0.075 | 4.15
13) | Garage, Parking |  |  | 200 |  | 5 | 0.0375 | 4.15
14) | Healthcare Facilities: |  | Sleeping Rooms | 120 |  | 8.3333 | 0.0625 | 4.15
|  |  | Treatment Rooms | 240 |  | 4.1667 | 0.03125 | 4.15
15) | Hotels and Apartments |  |  | 200 |  | 5 | 0.0375 | 4.15
|  |  | Hotel Function Area 3 | 7 |  | 142.8571 | 1.0714 | 4.15
|  |  | Hotel Lobby | 100 |  | 10 | 0.075 | 4.15
|  |  | Hotel Guest Rooms (<500 ft²) | 200 |  | 5 | 0.04 | Footnote 4
|  |  | Hotel Guest rooms (>=500 ft²) | 200 |  | 5 | 0.0375 | 4.15
| Occupancy |  | Use | CBC Occupancy Load (ft²/occ) |  | CBC Occupancy Load | CBC Based Ventilation (cfm/ft²)7 | Ventilation from Table 121-A (cfm/ft²)
(occ/1000 ft²)6
|  |  | Highrise Residential | 200 |  | 5 | 0.04 | Footnote 5
16) | Kitchen(s) |  |  | 200 |  | 5 | 0.0375 | 4.15
17) | Library: |  | Reading Rooms | 50 |  | 20 | 0.15 | 4.15
|  |  | Stack Areas | 100 |  | 10 | 0.075 | 4.15
18) | Locker Rooms |  |  | 50 |  | 20 | 0.15 | 4.15
19) | Manufacturing |  |  | 200 |  | 5 | 0.0375 | 4.15
20) | Mechanical Equipment Room |  |  | 300 |  | 3.3333 | 0.025 | 4.15
21) | Nurseries for Children - Day Care |  |  | 35 |  | 28.5714 | 0.21429 | 4.15
22) | Offices: |  | Office | 100 |  | 10 | 0.075 | 4.15
|  |  | Bank/Financial Institution | 100 |  | 10 | 0.075 | 4.15
|  |  | Medical & Clinical Care | 100 |  | 10 | 0.075 | 4.15
23) | Retail Stores (See Stores)
24) | School Shops & Vocational Rooms |  |  | 50 |  | 20 | 0.15 | 4.15
25) | Skating Rinks: |  | Skate Area | 50 |  | 20 | 0.15 | 4.15
|  |  | On Deck | 15 |  | 66.6667 | 0.5 | 4.15
26) | Stores: |  | Retail Sales, Wholesale Showrooms | 30 |  | 33.3333 | 0.25 | 4.15
|  |  | Basement and Ground Floor | 30 |  | 33.3333 | 0.25 | 4.15
|  |  | Upper Floors | 60 |  | 16.6667 | 0.125 | 4.15
|  |  | Grocery | 30 |  | 33.3333 | 0.25 | 4.15
|  |  | Malls, Arcades, & Atria | 30 |  | 33.3333 | 0.25 | 4.15
27) | Swimming Pools: |  | Pool Area | 50 |  | 20 | 0.15 | 4.15
|  |  | On Deck | 15 |  | 66.6667 | 0.5 | 4.15
28) | Warehouses, Industrial & Commercial Storage/Stockrooms |  |  | 500 |  | 2 | 0.015 | 4.15
29) | All Others -- Including Unknown |  |  | 100 |  | 10 | 0.075 | 4.15
|  |  | Corridors, Restrooms, & Support Areas | 100 |  | 10 | 0.075 | 4.15
|  |  | Commercial & Industrial Work | 100 |  | 10 | 0.075 | 4.15
Footnotes: |  |  |  |  | Equations used to find:
1. Convention, Conference, Meeting Rooms
2. Bars, Cocktail & Smoking Lounges, Casinos
3. See Conference Rooms or Dining Rooms
4. Guestrooms less than 500 ft² use 30 cfm/guestroom
5. Highrise Residential See 1994 UBC Section 1203 Ventilation

## Comparison (hidden)
2013 NACM Space Type | COMNET People | Notes | CBC People | Egress Occupancy Multiplier | CBC Adj Occupancy | Matching CBC Space Function | Recommended Occupancy | FINAL Occupancy | 2008 occupancy usable | occ based ventilation | Table 120.1 A over-rider | min ventilation from (floor & col.L) | CBC allottment | calc cbc density | All ppl
| # per 1000 ft² |  | # per 1000 ft² |  |  |  | # per 1000 ft²
Auditorium Area (Note 10) | 143 |  | n/a | 1 | 999 | n/a | 143 |  | 143 | 2.145 |  | 2.145 | 7 | 142.8571 | 143
Auto Repair Area | 10 |  | 10 | 0.5 | 5 | Auto Repair | 5 |  | 10 | 0.075 | 1.5 | 1.5 | 100 | 10 | 10
Bar, Cocktail Lounge and Casino Areas (Note 10) | 67 |  | 67 | 0.5 | 33.5 | Drinking Establishments | 33.5 |  | 67 | 0.5025 | 0.2 | 0.5025 | 15 | 66.6667 | 67
Beauty Salon Area | 10 |  | 10 | 0.5 | 5 | Barber & Beauty Shops | 5 |  | 10 | 0.075 | 0.4 | 0.4 | 100 | 10 | 10
Classrooms, Lecture, Training, Vocational Areas | 50 |  | 50 | 0.5 | 25 | Classrooms | 25 |  | 50 | 0.375 |  | 0.375 | 20 | 50 | 50
Civic Meeting Place Area (Note 10) | 25 |  | 67 | 0.5 | 33.5 | Lobbies | 33.5 |  | 25 | 0.1875 |  | 0.1875 | 40 | 25 | 67
Commercial and Industrial Storage Areas (conditioned or unconditioned) | 3 |  | 2 | 0.5 | 1 | Warehouses, Industrial & Commercial Storage/Stockrooms | 1 |  | 3 | 0.0225 |  | 0.15 | 300 | 3.3333 | 3
Commercial and Industrial Storage Areas (refrigerated) | 0 |  | n/a |  | 999 |  | 0 |  | 1 | 0 |  | 0.15 | 500 | 2 | 0
Computer Room (Note 11) | 3 | SpcFunc only valid if user-input receptacle load is >= 20W/ft2 | n/a |  | 999 |  | 3 |  | 20 | 0 |  | 0.15 | 50 | 20 | 3
Convention, Conference, Multipurpose and Meeting Center Areas (Note 10) | 67 |  | 67 | 0.5 | 33.5 | Assembly Areas (Nonconcentrated Use) | 33.5 |  | 67 | 0.5025 |  | 0.5025 | 15 | 66.6667 | 67
Corridors, Restrooms, Stairs, and Support Areas | 10 |  | n/a |  | 999 |  | 10 |  | 10 | 0 |  | 0.15 |  |  | 10
Dining Area (Note 10) | 67 |  | n/a |  | 999 |  | 67 |  | 67 | 0 |  | 0.15 | 15 | 66.6667 | 67
Dry Cleaning (Coin Operated) | 10 |  | 10 | 0.5 | 5 | Dry Cleaning (Coin-Operated) | 5 |  | 10 | 0.075 | 0.3 | 0.3 | 100 | 10 | 10
Dry Cleaning (Full Service Commercial) | 10 |  | 10 | 0.5 | 5 | Dry Cleaning (Commercial) | 5 |  | 10 | 0.075 | 0.45 | 0.45 | 100 | 10 | 10
Electrical, Mechanical, Telephone Rooms | 3 |  | 3 | 0.5 | 1.5 | Mechanical Equipment Room | 1.5 |  | 3 | 0.0225 |  | 0.15 | 300 | 3.3333 | 3
Exercise Center, Gymnasium Areas | 67 |  | 67 | 0.5 | 33.5 | Gymnasiums/Sports Arenas | 33.5 |  | 20 | 0.15 |  | 0.15 | 50 | 20 | 67
Exhibit, Museum Areas (Note 10) | 67 |  | 67 | 0.5 | 33.5 | Exhibit/Display Areas | 33.5 |  | 67 | 0.5025 |  | 0.5025 | 15 | 66.6667 | 67
Financial Transaction Area | 10 |  | 10 | 0.5 | 5 | Bank/Financial Institution | 5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 10
General Commercial and Industrial Work Areas, High Bay | 10 |  | 5 | 0.5 | 2.5 | Manufacturing | 2.5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 10
General Commercial and Industrial Work Areas, Low Bay | 10 |  | 5 | 0.5 | 2.5 | Manufacturing | 2.5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 10
General Commercial and Industrial Work Areas, Precision | 10 |  | 5 | 0.5 | 2.5 | Manufacturing | 2.5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 10
Grocery Sales Areas (Note 10) | 33 |  | 33 | 0.5 | 16.5 | Grocery | 16.5 |  | 33 | 0.2475 | 0.2 | 0.2475 |  |  | 33
High-Rise Residential Living Spaces (Note 9) | 5 |  | 5 | 1 | 5 | Hotel Guestrooms | 5 |  | 5 | 0.075 | see special note | 0.15 | 200 | 5 | 5
Hotel Function Area (Note 10) | 67 |  | 143 | 0.5 | 71.5 | Hotel Function Area | 71.5 |  | 67 | 0.5025 |  | 0.5025 |  |  | 143
Hotel/Motel Guest Room (Note 9) | 5 |  | 5 | 1 | 5 | Hotel Guestrooms | 5 |  | 5 | 0.075 | see note | 0.15 | 200 | 5 | 5
Housing, Public and Common Areas: Multi-family, Dormitory | 10 |  | 20 | 0.5 | 10 | Dormitories | 10 |  | 10 | 0.075 |  | 0.15 |  |  | 20
Housing, Public and Common Areas: Senior Housing | 10 |  | 8 | 1 | 8 | Children's Homes & Homes for Aged | 8 |  | 10 | 0.15 |  | 0.15 |  |  | 10
Kitchen, Commercial Food Preparation | 5 | GasEquipPwr only valid if hood length > 0. If there is an exhaust hood, set convective fraction to 0 | 5 | 0.5 | 2.5 | Kitchen(s) | 2.5 |  | 5 | 0.0375 |  | 0.15 | 200 | 5 | 5
Kitchenette or Residential Kitchen | 5 |  | 5 | 0.5 | 2.5 | Kitchen(s) | 2.5 |  | 5 | 0.0375 |  | 0.15 | 200 | 5 | 5
Laboratory, Scientific | 10 |  | n/a |  | 999 |  | 10 |  | 10 | 0 | 0.38 | 0.15 | 100 | 10 | 10
Laboratory, Equipment Room | 5 |  | n/a |  | 999 |  | 5 |  | 5 | 0 |  | 0.15 | 200 | 5 | 5
Laundry | 10 |  | n/a |  | 999 |  | 10 |  | 10 | 0 |  | 0.15 | 100 | 10 | 10
Library, Reading Areas | 20 |  | 20 | 0.5 | 10 | Library, Reading Areas | 10 |  | 20 | 0.15 |  | 0.15 | 50 | 20 | 20
Library, Stacks | 10 |  | 10 | 0.5 | 5 | Library, Stacks | 5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 10
Lobby, Hotel | 10 |  | 67 | 0.5 | 33.5 | Assembly Areas (Concentrated Use), Lobbies | 33.5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 67
Lobby, Main Entry | 10 |  | 67 | 0.5 | 33.5 |  | 33.5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 67
Locker/Dressing Room | 20 |  | 20 | 0.5 | 10 | Locker Rooms | 10 |  | 20 | 0.15 |  | 0.15 | 50 | 20 | 20
Lounge, Recreation (Note 10) | 67 |  | 67 | 0.5 | 33.5 | Assembly Areas (Nonconcentrated Use), Lounges | 33.5 |  | 67 | 0.5025 |  | 0.5025 | 15 | 66.6667 | 67
Malls and Atria (Note 10) | 33 |  | 33.3333 | 0.5 | 16.6667 | Stores: Malls, Arcades, & Atria | 16.7 |  | 33 | 0.2475 |  | 0.2475 | 30 | 33.3333 | 33.3333
Medical and Clinical Care | 10 |  | 10 | 0.5 | 5 | Office: Medical and Clinical Care | 5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 10
Office (Greater than 250 square feet in floor area) | 10 |  | 10 | 0.5 | 5 | Office | 5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 10
Office (250 square feet in floor area or less) | 10 |  | 10 | 0.5 | 5 | Office | 5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 10
Parking Garage Building, Parking Area | 10 |  | 5 | 0.5 | 2.5 | Garage, Parking | 2.5 |  | 5 | 0.0375 |  | 0.15 | 200 | 5 | 10
Parking Garage Area Dedicated Ramps | 10 |  | 5 | 0.5 | 2.5 | Garage, Parking | 2.5 |  | 5 | 0.0375 |  | 0.15 | 200 | 5 | 10
Parking Garage Area Daylight Adaptation Zones | 10 |  | 5 | 0.5 | 2.5 | Garage, Parking | 2.5 |  | 5 | 0.0375 |  | 0.15 | 200 | 5 | 10
Police Station and Fire Station | 10 |  | n/a |  | 999 |  | 10 |  | 10 | 0 |  | 0.15 | 100 | 10 | 10
Religious Worship Area (Note 10) | 143 |  | 143 | 1 | 143 | Churches & Chapels (Religious Worship) | 143 |  | 143 | 2.145 |  | 2.145 | 7 | 142.8571 | 143
Retail Merchandise Sales, Wholesale Showroom (Note 10) | 33 |  | 33 | 0.5 | 16.5 | Retail Sales, Wholesale Showrooms | 16.5 |  | 33 | 0.2475 | 0.2 | 0.2475 | 30 | 33.3333 | 33
Sports Arena, Indoor Playing Area | 143 |  | 67 | 0.5 | 33.5 | Gymnasiums/Sports Arenas | 33.5 |  |  | 0 |  | 0.15 |  |  | 143
Theater, Motion Picture (Note 10) | 143 |  | n/a |  | 999 |  | 143 |  | 143 | 0 |  | 0.15 | 7 | 142.8571 | 143
Theater, Performance (Note 10) | 143 |  | n/a |  | 999 |  | 143 |  | 143 | 0 |  | 0.15 | 7 | 142.8571 | 143
Transportation Function (Note 10) | 33 |  | n/a |  | 999 |  | 33 |  | 33 | 0 |  | 0.15 |  |  | 33
Unoccupied-Exclude from Gross Floor Area | 0 |  | n/a |  | 999 |  | 0 |  |  | 0 |  | 0.15 |  |  | 0
Unoccupied-Include in Gross Floor Area | 0 |  | n/a |  | 999 |  | 0 |  |  | 0 |  | 0.15 |  |  | 0
Videoconferencing Studio (Note S1) | 10 |  | n/a |  | 999 |  | 10 |  |  | 0 |  | 0.15 |  |  | 10
Waiting Area | 10 |  | ??? |  |  |  | 10 |  | 10 | 0 |  | 0.15 |  |  | 10
All Others (including unleased tenant space in multi-tenant facilities) | 10 | [5 empty] | 10 |  | 10 | 0 |  | 0.15 |  |  | 10